Harbourline Energy Co.

# Vegetation Management Procedure

| Field | Value |
| --- | --- |
| Document ID | OPS-PRO-009 |
| Revision | 6 |
| Effective date | April 1, 2026 |
| Next review | April 1, 2027 |
| Document owner | Colleen Yarrow, Manager, Forestry and Vegetation Management |
| Approved by | Renata Okafor, Director, Distribution Operations |
| Applies to | Forestry staff, line clearance contractors and planners in all regions |

# 1. Purpose

Trees contacting power lines are the leading cause of outage minutes on the Harbourline distribution system. This procedure sets the trim cycles, clearance distances, hazard tree practices and customer notification rules that Harbourline and its line clearance contractors follow.

# 2. Scope

The procedure applies to all overhead transmission, sub-transmission and distribution lines in Ontario, New York and Ohio. Transmission lines operated at 200 kV and above are also managed to meet NERC FAC-003 requirements, which take precedence where they are more stringent.

# 3. Trim Cycles by Circuit Type

The trim cycle is the planned interval between full maintenance trims on the same circuit. Cycles are set by circuit type and area.

| Circuit type | Typical voltage | Urban cycle | Rural cycle | Patrol |
| --- | --- | --- | --- | --- |
| Transmission right of way | 115 kV, 138 kV, 230 kV | 5 years | 5 years | Aerial patrol twice a year; LiDAR survey every 2 years |
| Sub-transmission | 44 kV (ON), 34.5 kV (NY, OH) | 4 years | 4 years | Ground patrol annually |
| Three phase distribution mainline | 27.6 kV, 13.8 kV, 13.2 kV, 12.47 kV | 3 years | 4 years | Ground patrol annually |
| Single phase lateral | 16 kV, 8 kV, 7.6 kV, 7.2 kV | 5 years | 6 years | Visual check at each trim |
| Secondary and service drops | 120/240 V, 347/600 V | On request | On request | Reactive only |

## 3.1 Cycle acceleration

Any feeder in the worst performing 5 percent by tree caused customer interruptions over the last 3 years is trimmed in the next work plan year regardless of its cycle position.

# 4. Clearance Distances at Time of Trim

Clearances are measured from the nearest conductor at maximum sag. The side clearance applies horizontally; overhang is removed above the conductor to the height shown.

| Circuit type | Side clearance | Below conductor | Overhang removal above conductor |
| --- | --- | --- | --- |
| Transmission 230 kV | 9.0 m (30 ft) | Full ROW floor clearing | Remove all overhang |
| Transmission 115 kV and 138 kV | 7.5 m (25 ft) | Full ROW floor clearing | Remove all overhang |
| Sub-transmission 34.5 kV and 44 kV | 4.5 m (15 ft) | 3.0 m (10 ft) | Remove all overhang |
| Three phase mainline | 3.0 m (10 ft) | 3.0 m (10 ft) | 4.5 m (15 ft) |
| Single phase lateral | 2.5 m (8 ft) | 2.5 m (8 ft) | 3.0 m (10 ft) |
| Secondary and services | 0.5 m (1.5 ft) and no strain on the conductor | Not specified | Not specified |

# 5. Hazard Trees

A hazard tree is a dead, dying, leaning, cracked or otherwise defective tree, inside or outside the trim zone, that could strike a conductor if it or part of it fails. Crews record hazard trees in the mobile vegetation application with a photo and a risk score from 1 (low) to 5 (imminent).

Risk score 5: removed or made safe within 48 hours; the DSO is notified immediately.

Risk score 4: removed within 30 calendar days.

Risk score 3 or lower: scheduled with the next cycle trim.

Ash trees killed by emerald ash borer within striking distance of three phase lines are treated as risk score 4.

# 6. Customer and Landowner Notification

| Jurisdiction | Notice before routine work | Method |
| --- | --- | --- |
| Ontario | At least 14 calendar days | Door hanger and letter |
| New York | At least 10 calendar days | Door hanger; letter to absentee owners |
| Ohio | At least 7 calendar days | Door hanger and phone call |

No advance notice is required for emergency work to remove an immediate hazard or restore service. Landowners who refuse access are referred to the Forestry Supervisor, who documents the refusal and any resulting reliability risk.

# 7. Work Methods

Directional pruning to the branch collar following ANSI A300 practices; no topping or rounding over.

Herbicide use on rights of way only by licensed applicators and only with products approved by the applicable provincial or state authority.

Only line clearance qualified arborists work within 3.0 m (10 ft) of energized distribution conductors.

Wood chips are left on site only with the owner's consent.

# 8. Performance Measures

| Measure | 2026 target |
| --- | --- |
| Tree caused customer interruptions per 100 km of overhead line | 18 or fewer |
| Planned trim kilometres completed | Ontario 4,200 km; New York 1,150 km; Ohio 980 km |
| Risk score 5 hazard trees made safe within 48 hours | 100 percent |

# Revision History

| Revision | Date | Author | Summary of changes |
| --- | --- | --- | --- |
| 5 | 2024-03-15 | C. Yarrow | Added emerald ash borer guidance. |
| 6 | 2026-04-01 | C. Yarrow | Rural lateral cycle extended from 5 to 6 years; updated 2026 targets. |