Harbourline Energy Co.

# Field Report

| Field | Value |
| --- | --- |
| Report ID | FR-EON-2026-1187 |
| Date | 2026-10-01 |
| Region | Eastern Ontario |
| Crew ID | CREW-ON-03 |
| Crew leader | Devon Achebe |
| Asset ID | TX-ON-10423 |
| Asset description | 25 kVA pole-mount transformer, model NF-PM25-16B, pole P-30912, Bath Road near Collins Bay Road, Kingston ON |
| Issue | Oil weeping from the tank lid gasket, dark stain on the pole below the tank. No customer outage. |
| Severity | Moderate |
| Recommended action | Schedule planned replacement within 10 business days and add spill tray inspection to the work order. |

# Crew notes

Found during routine pole inspection patrol on feeder KNG-M4. Tank temperature normal by infrared scan. Oil level sight glass reads low but visible. Customers on the transformer were not interrupted. Area around the pole base is gravel, no watercourse within 50 m.

# Submission

Submitted from the mobile workforce application to the Procedures/Incoming folder for triage by the Operations Triage agent.