Harbourline Energy Co.

# Field Report

| Field | Value |
| --- | --- |
| Report ID | FR-NYN-2026-0442 |
| Date | 2026-10-02 |
| Region | New York North Country |
| Crew ID | CREW-NY-13 |
| Crew leader | Colleen Brady |
| Asset ID |  |
| Asset description | Pole-mount transformer on the east side of Arsenal Street near the Coffeen Street intersection, Watertown NY. Asset tag missing from the tank. |
| Issue | Squirrel guard missing on the primary bushing; evidence of animal contact and a blown cutout fuse that was refused once overnight by the trouble crew. |
| Severity | Low |
| Recommended action | Install a new wildlife guard and replace the asset tag at the next planned visit; records team to confirm the asset ID from GIS. |

# Crew notes

Trouble crew restored service to 9 customers at 02:40 by replacing the cutout fuse. No asset tag could be read on the tank, so the asset ID field is left blank for records to complete.

# Submission

Submitted from the mobile workforce application to the Procedures/Incoming folder for triage by the Operations Triage agent.